## Oscillation Mining Results
Executive Summary for the period March 18, 2017 - March 30, 2017
Band | Root Cause | Mode Range (Hz) | Count of PMU Locations | Count of Events | Count of Modes
1 | Speed Governor | 0.01 to 0.15
2 | Inter-area Oscillations | 0.16 to 1.0 | 13 | 25 | 7
3 | Local Plant Control Systems | 1.1 to 5.0 | 3 | 2 | 2
4 | Controllers | 5.1 to 15 | 3 | 15 | 4
Oscillation Event Mining Results
PMU Locations | Counts of Events by PMU Location | Count of Events by Mode | Mode (Hz) | Peak-to-Peak Magnitude of Oscillation by Metric
PMU1 | 14 | 6 | 6 | 0.02 Hz
PMU1 | 14 | 5 | 6.5 | 0.03 Hz
PMU1 | 14 | 3 | 7 | 0.03 Hz
PMU2 | 9 | 3 | 0.6 | 77.3 Amps
PMU2 | 9 | 3 | 0.7 | 88.7 Amps
PMU2 | 9 | 1 | 0.3 | 10.6 Amps
PMU2 | 9 | 1 | 0.6 | 1.1 kV
PMU2 | 9 | 1 | 1 | 12.0 Amps
PMU3 | 4 | 1 | 0.5 | 14.0 Amps
PMU3 | 4 | 1 | 0.6 | 14.6 Amps
PMU3 | 4 | 1 | 1.6 | 10.4 Amps
PMU3 | 4 | 1 | 5.5 | 12.2 Amps
PMU4 | 4 | 1 | 0.5 | 13.8 Amps
PMU4 | 4 | 1 | 0.7 | 14.5 Amps
PMU4 | 4 | 1 | 1.6 | 10.5 Amps
PMU4 | 4 | 1 | 5.5 | 12.2 Amps
PMU5 | 4 | 2 | 0.7 | 11.7 Amps
PMU5 | 4 | 1 | 0.6 | 16.6 Amps
PMU5 | 4 | 1 | 0.8 | 13.9 Amps
PMU6 | 2 | 2 | 1 | 18.9 Amps
PMU7 | 2 | 2 | 0.7 | 14.6 Amps
PMU8 | 2 | 2 | 0.7 | 14.5 Amps
PMU9 | 2 | 2 | 1 | 12.6 Amps
PMU10 | 1 | 1 | 0.8 | 20.0 Amps
PMU11 | 1 | 1 | 0.8 | 18.4 Amps
PMU12 | 1 | 1 | 0.8 | 12.6 Amps
PMU13 | 1 | 1 | 0.9 | 11.3 Amps
PMU14 | 1 | 1 | 0.6 | 10.1 Amps
PMU15 | 1 | 1 | 1.2 | 1.0 kV

## Oscillation Events
Oscillation Events Listing for the period March 18, 2017 - March 30, 2017
SignalName | SignalType | Event Start Time | Event End Time | Mode (Hz) | Peak-to-Peak Magnitude
PMU1.Frequency.FR | FR | 2017-03-18 13:19 | 2017-03-18 13:25 | 6 | 0.01392
PMU2.I1.IM | IM | 2017-03-18 21:46 | 2017-03-18 21:50 | 0.3 | 10.62
PMU1.Frequency.FR | FR | 2017-03-19 06:46 | 2017-03-19 06:53 | 6 | 0.018098
PMU1.Frequency.FR | FR | 2017-03-19 17:16 | 2017-03-19 17:20 | 6 | 0.019759
PMU3.IASPM.IM | IM | 2017-03-19 20:52 | 2017-03-19 20:58 | 0.6 | 13.8013
PMU3.ICSPM.IM | IM | 2017-03-19 20:54 | 2017-03-19 20:58 | 0.55 | 13.9531
PMU3.I1SPM.IM | IM | 2017-03-19 20:54 | 2017-03-19 20:58 | 0.6 | 13.9419
PMU4.I1SPM.IM | IM | 2017-03-19 20:54 | 2017-03-19 20:58 | 0.55 | 13.7909
PMU4.ICSPM.IM | IM | 2017-03-19 20:54 | 2017-03-19 20:58 | 0.65 | 13.7552
PMU1.Frequency.FR | FR | 2017-03-20 11:35 | 2017-03-20 11:39 | 6.5 | 0.018196
PMU6.ICSPM.IM | IM | 2017-03-20 14:15 | 2017-03-20 14:19 | 1 | 10.3806
PMU1.Frequency.FR | FR | 2017-03-20 16:46 | 2017-03-20 16:59 | 6.5 | 0.028499
PMU1.Frequency.FR | FR | 2017-03-20 17:09 | 2017-03-20 17:14 | 6 | 0.018447
PMU1.Frequency.FR | FR | 2017-03-20 17:16 | 2017-03-20 17:24 | 7 | 0.01859
PMU4.ICSPM.IM | IM | 2017-03-20 17:30 | 2017-03-20 17:34 | 1.6 | 10.5163
PMU3.ICSPM.IM | IM | 2017-03-20 17:30 | 2017-03-20 17:34 | 1.6 | 10.4033
PMU5.I1WPM.IM | IM | 2017-03-21 00:49 | 2017-03-21 00:53 | 0.75 | 11.6627
PMU3.ICSPM.IM | IM | 2017-03-21 12:20 | 2017-03-21 12:25 | 0.65 | 14.5662
PMU4.ICSPM.IM | IM | 2017-03-21 12:20 | 2017-03-21 12:25 | 0.7 | 14.4911
PMU3.IBSPM.IM | IM | 2017-03-21 12:20 | 2017-03-21 12:25 | 0.65 | 14.1873
PMU7.ICSPM.IM | IM | 2017-03-21 13:49 | 2017-03-21 13:53 | 0.7 | 14.5822
PMU8.ICSPM.IM | IM | 2017-03-21 13:49 | 2017-03-21 13:53 | 0.7 | 14.5174
PMU7.I1SPM.IM | IM | 2017-03-21 13:49 | 2017-03-21 13:55 | 0.9 | 14.307
PMU8.I1SPM.IM | IM | 2017-03-21 13:49 | 2017-03-21 13:55 | 0.9 | 14.2373
PMU8.IBSPM.IM | IM | 2017-03-21 13:49 | 2017-03-21 13:55 | 0.9 | 14.1314
PMU8.IASPM.IM | IM | 2017-03-21 13:49 | 2017-03-21 13:55 | 0.9 | 14.0115
PMU7.IBSPM.IM | IM | 2017-03-21 13:49 | 2017-03-21 13:55 | 0.9 | 14.0042
PMU7.IASPM.IM | IM | 2017-03-21 13:49 | 2017-03-21 13:53 | 0.7 | 13.589
PMU7.ICSPM.IM | IM | 2017-03-21 21:46 | 2017-03-21 21:50 | 0.7 | 11.0203
PMU8.ICSPM.IM | IM | 2017-03-21 21:46 | 2017-03-21 21:50 | 0.7 | 10.7748
PMU7.I1SPM.IM | IM | 2017-03-21 21:46 | 2017-03-21 21:50 | 0.7 | 10.6157
PMU7.IBSPM.IM | IM | 2017-03-21 21:46 | 2017-03-21 21:50 | 0.7 | 10.4402
PMU8.I1SPM.IM | IM | 2017-03-21 21:46 | 2017-03-21 21:50 | 0.7 | 10.4064
PMU4.IBSPM.IM | IM | 2017-03-22 00:23 | 2017-03-22 00:27 | 5.5 | 12.1725
PMU3.IBSPM.IM | IM | 2017-03-22 00:23 | 2017-03-22 00:27 | 5.5 | 12.1656
PMU5.I1WPM.IM | IM | 2017-03-22 00:30 | 2017-03-22 00:34 | 0.8 | 13.944
PMU2.I1.IM | IM | 2017-03-22 00:36 | 2017-03-22 00:44 | 0.65 | 38.042
PMU2.I1.IM | IM | 2017-03-22 09:09 | 2017-03-22 09:14 | 0.7 | 88.7289
PMU2.I1.IM | IM | 2017-03-22 09:31 | 2017-03-22 09:38 | 0.7 | 73.9648
PMU5.I1WPM.IM | IM | 2017-03-22 14:01 | 2017-03-22 14:05 | 0.7 | 11.5089
PMU2.I1.IM | IM | 2017-03-23 03:09 | 2017-03-23 03:13 | 1 | 11.961
PMU6.I1SPM.IM | IM | 2017-03-23 07:15 | 2017-03-23 07:19 | 1 | 18.8773
PMU10.ICSPM.IM | IM | 2017-03-23 11:20 | 2017-03-23 11:24 | 0.8 | 20.0379
PMU11.IASPM.IM | IM | 2017-03-23 11:20 | 2017-03-23 11:24 | 0.85 | 18.4392
PMU10.I1SPM.IM | IM | 2017-03-23 11:20 | 2017-03-23 11:24 | 0.8 | 17.6542
PMU11.I1SPM.IM | IM | 2017-03-23 11:20 | 2017-03-23 11:24 | 0.85 | 17.3954
PMU10.IASPM.IM | IM | 2017-03-23 11:20 | 2017-03-23 11:24 | 0.85 | 16.5112
PMU10.IBSPM.IM | IM | 2017-03-23 11:20 | 2017-03-23 11:24 | 0.8 | 16.3838
PMU11.IBSPM.IM | IM | 2017-03-23 11:20 | 2017-03-23 11:24 | 0.8 | 16.1311
PMU12.IBSPM.IM | IM | 2017-03-23 11:37 | 2017-03-23 11:41 | 0.85 | 12.6036
PMU12.I1SPM.IM | IM | 2017-03-23 11:37 | 2017-03-23 11:41 | 0.8 | 12.4642
PMU12.ICSPM.IM | IM | 2017-03-23 11:37 | 2017-03-23 11:41 | 1 | 12.0646
PMU13.IASPM.IM | IM | 2017-03-23 11:37 | 2017-03-23 11:41 | 0.9 | 11.3276
PMU9.IASPM.IM | IM | 2017-03-23 17:06 | 2017-03-23 17:12 | 1 | 12.5561
PMU9.IBSPM.IM | IM | 2017-03-23 17:06 | 2017-03-23 17:12 | 1 | 12.5334
PMU9.I1SPM.IM | IM | 2017-03-23 17:06 | 2017-03-23 17:12 | 1 | 12.5131
PMU9.ICSPM.IM | IM | 2017-03-23 17:06 | 2017-03-23 17:12 | 1 | 12.4619
PMU1.Frequency.FR | FR | 2017-03-23 17:30 | 2017-03-23 17:36 | 7 | 0.026553
PMU9.IASPM.IM | IM | 2017-03-23 19:00 | 2017-03-23 19:05 | 1 | 10.9105
PMU9.ICSPM.IM | IM | 2017-03-23 19:00 | 2017-03-23 19:05 | 1 | 10.8682
PMU9.I1SPM.IM | IM | 2017-03-23 19:00 | 2017-03-23 19:05 | 1 | 10.84
PMU9.IBSPM.IM | IM | 2017-03-23 19:00 | 2017-03-23 19:05 | 1 | 10.7775
PMU5.I1WPM.IM | IM | 2017-03-23 23:08 | 2017-03-23 23:12 | 0.6 | 16.5624
PMU1.Frequency.FR | FR | 2017-03-24 17:38 | 2017-03-24 17:44 | 6.5 | 0.028694
PMU2.I1.IM | IM | 2017-03-25 18:09 | 2017-03-25 18:14 | 0.6 | 77.252
PMU2.V1.VM | VM | 2017-03-25 18:09 | 2017-03-25 18:14 | 0.6 | 1.0613
PMU2.I1.IM | IM | 2017-03-25 18:15 | 2017-03-25 18:19 | 0.7 | 67.3596
PMU2.I1.IM | IM | 2017-03-25 18:21 | 2017-03-25 18:27 | 0.65 | 75.9997
PMU1.Frequency.FR | FR | 2017-03-26 11:25 | 2017-03-26 11:29 | 6 | 0.012672
PMU1.Frequency.FR | FR | 2017-03-27 09:50 | 2017-03-27 09:58 | 6 | 0.012016
PMU2.I1.IM | IM | 2017-03-27 14:30 | 2017-03-27 14:37 | 0.4 | 39.516
PMU2.I1.IM | IM | 2017-03-27 14:38 | 2017-03-27 14:44 | 0.7 | 61.7907
PMU2.I1.IM | IM | 2017-03-27 14:45 | 2017-03-27 14:50 | 0.6 | 73.7172
PMU14.ICSPM.IM | IM | 2017-03-28 14:34 | 2017-03-28 14:38 | 0.65 | 10.1148
PMU1.Frequency.FR | FR | 2017-03-28 17:00 | 2017-03-28 17:07 | 7 | 0.020614
PMU2.I1.IM | IM | 2017-03-28 23:08 | 2017-03-28 23:13 | 0.7 | 57.9605
PMU15.VAPM.VM | VM | 2017-03-29 00:53 | 2017-03-29 00:57 | 1.2 | 1.011
PMU1.Frequency.FR | FR | 2017-03-29 17:18 | 2017-03-29 17:24 | 6.5 | 0.023903
PMU1.Frequency.FR | FR | 2017-03-29 17:30 | 2017-03-29 17:42 | 6.5 | 0.021663